CONTRACTOR SUBMITTED QUESTIONS AND RESPONSES

Bid #51 - US-431 Attalla Underpass Pump System Replacement

This document summarizes questions submitted by the potential proposers to the ALDOT Procurement Office and the ALDOT’s responses.

Q: Does the natural gas back up pump require hardened wear parts?

Response: Hardened wear parts are not specifically required but may be included in the proposal if they can be shown to increase or contribute to the lifespan of the system.

Q: All hatch covers require safety grates?

Response: Yes.

Q: Air gas monitor to be built in the panel. Do they want it measuring the upper room or lower well?

Response: The location of an air/gas monitor is up to the proposer. This should be the best fit location for the proposer’s ventilation plan or to industry standards.

Q: The natural gas pump needs to exercise weekly. This will need to be tied into the panel.

Response: Yes.

Q: All steel in the lower level need to be SS?

Response: The material selection is up to the proposer, and the expected durability should be referenced in the proposal.

Q: Do they want a call out box built into panel? Put it as an additional line item?

Response: An optional line item may be included for a simple notification system in the case of a high-water alarm or pump failure. Full remote diagnostics are not required.

Q: Who is responsible for the bypass while work is being performed? This includes the existing bypass that is set in place currently.

Response: The in-place rental pump will remain until a startup can be coordinated for the new system.

Q: Are there any requirements for bonding or permitting from the railroad company given the proximity to work to the railroad?

Response: No.

Q: As built drawings required upon completion of work?

Response: Yes.

Q: Will a bid bond be required?

Response: No.

Q: What permitting will be required from the city on the project?

Response: Any applicable local permit requirements with the City of Attalla are the responsibility of the contractor.

Q: Does any structural alterations to the lift station need to be reviewed by a structural engineer?

Response: As structural details of the lift station are not readily available, any structural alterations are at the contractor’s assumed risk, and it may be in the contractor’s best interest that a review be included by the contractor subsidiary to the work items. If so, please make a reference with the contractor’s approach in the proposal.

All electrical work needs to be performed by licensed electricians?

Response: Per the Notice of Need, All electrical requirements shall meet local and state electrical codes and be performed by a certified electrician. More specifically, any connections made to the utility provider’s service are required to be made by a licensed electrician. Contractor technicians may complete installation work within the new pump system given the workmanship is of a professional quality and standard as generally accepted in the trade.